## 22.10.2018 Test
Verification of AWS flow meters through readings from Ultrasonic (U-S) Flow Meter
| Date | 22.10.2018
| Starting Time | 4.19 pm
| Ending Time | 4.34 pm
| Duration | 15 minutes
| Minutes | U-S Readings
| 1 | 9.1906
| 2 | 9.0917
| 3 | 9.0363
| 4 | 8.7577
| 5 | 8.8389
| 6 | 8.6223
| 7 | 8.5611
| 8 | 8.4543
| 9 | 8.3
| 10 | 8.2203
| 11 | 8.0953
| 12 | 8.0998
| 13 | 8.0862
| 14 | 7.9478
| 15 | 7.8211
| Total | 127.1234 | Average | 8.4749
AWS flow meter
starting reading (cubic meters) |  |  |  | 34575.56
ending reading (cubic meters) |  |  |  | 34577.873
water flowing in 15 minutes (cubic meters) |  |  |  | 2.313
water flowing in one hour (cubic meters) |  |  |  | 9.252
U-S flow meter
water flowing in one hour (cubic meters) |  |  |  | 8.4749
Difference between Ultrasonic flowmeter readings average and AWS meter (cubic meters) |  |  |  | 0.77711
RESULT
AWS meter is measuring 0.777 cubic meters per hour more than U-S flow meter (about 9%)
AWS meter - Starting Reading |  |  | AWS meter - Ending Reading

## 29.10.2018 Test
Verification of AWS flow meters through readings from Ultrasonic (U-S) Flow Meter
| Date | 29.10.2018
| Starting Time | 3.48 pm
| Ending Time | 4.17 pm
| Duration | 30 minutes
| Minutes | U-S Readings |  | AWS meter - Starting Reading
| 1 | 8.3507
| 2 | 8.2758
| 3 | 8.1516
| 4 | 8.0431
| 5 | 8.005
| 6 | 7.9197
| 7 | 7.7432
| 8 | 7.702
| 9 | 7.7941
| 10 | 7.6435
| 11 | 7.457
| 12 | 7.449
| 13 | 7.5347
| 14 | 7.4411
| 15 | 7.3345
| 16 | 7.2884
| 17 | 7.1431 |  | AWS meter - Ending Reading
| 18 | 7.1821
| 19 | 6.9749
| 20 | 7.0511
| 21 | 6.9799
| 22 | 6.8729
| 23 | 6.7818
| 24 | 6.712
| 25 | 6.7492
| 26 | 6.6235
| 27 | 6.5313
| 28 | 6.4949
| 29 | 6.3573
| 30 | 6.5394
| Total | 219.1268 | Average | 7.3042
AWS flow meter
starting reading (cubic meters) |  |  |  | 34950.957
ending reading (cubic meters) |  |  |  | 34955.091
water flowing in 30 minutes (cubic meters) |  |  |  | 4.134
water flowing in one hour (cubic meters) |  |  |  | 8.268
U-S flow meter
water flowing in one hour (cubic meters) |  |  |  | 7.3042
Difference between Ultrasonic flowmeter readings average and AWS meter (cubic meters) |  |  |  | 0.96377
RESULT
AWS meter is measuring 0.96 cubic meters per hour more than U-S flow meter (about 13%)

## 03.11.2018 Test 1
Verification of AWS flow meters through readings from Ultrasonic (U-S) Flow Meter
| Date | 03.11.2018
| Starting Time | 10.45 am
| Ending Time | 11.00 am
| Duration | 15 minutes
| Minutes | U-S Readings
| 1 | 10.483
| 2 | 10.52
| 3 | 10.103
| 4 | 9.9548
| 5 | 9.7263
| 6 | 9.8214
| 7 | 9.6678
| 8 | 9.7164
| 9 | 9.5865
| 10 | 9.4094
| 11 | 9.435
| 12 | 9.2316
| 13 | 9.2373
| 14 | 9.1703
| 15 | 9.083
| Total | 145.1458 | Average | 9.6764
AWS flow meter
starting reading (cubic meters) |  |  |  | 35193.002
ending reading (cubic meters) |  |  |  | 35195.46
water flowing in 15 minutes (cubic meters) |  |  |  | 2.458
water flowing in one hour (cubic meters) |  |  |  | 9.832
U-S flow meter
water flowing in one hour (cubic meters) |  |  |  | 9.6764
Difference between Ultrasonic flowmeter readings average and AWS meter (cubic meters) |  |  |  | 0.15561
RESULT
AWS meter is measuring 0.156 cubic meters per hour more than U-S flow meter (about 1.2%)
AWS meter - Starting Reading |  |  | AWS meter - Ending Reading

## 03.11.2018 Test 2
Verification of AWS flow meters through readings from Ultrasonic (U-S) Flow Meter
| Date | 03.11.2018
| Starting Time | 11.25 am
| Ending Time | 11.40 am
| Duration | 15 minutes
| Minutes | U-S Readings
| 1 | 10.133
| 2 | 10.103
| 3 | 9.903
| 4 | 9.8242
| 5 | 9.7623
| 6 | 9.6474
| 7 | 9.4992
| 8 | 9.3499
| 9 | 9.1881
| 10 | 9.0772
| 11 | 9.1139
| 12 | 8.9761
| 13 | 8.9
| 14 | 8.7969
| 15 | 8.7375
| Total | 141.0117 | Average | 9.4008
AWS flow meter
starting reading (cubic meters) |  |  |  | 35196.009
ending reading (cubic meters) |  |  |  | 35198.388
water flowing in 15 minutes (cubic meters) |  |  |  | 2.379
water flowing in one hour (cubic meters) |  |  |  | 9.516
U-S flow meter
water flowing in one hour (cubic meters) |  |  |  | 9.4008
Difference between Ultrasonic flowmeter readings average and AWS meter (cubic meters) |  |  |  | 0.11522
RESULT
AWS meter is measuring 0.115 cubic meters per hour more than U-S flow meter (about 1.2%)
AWS meter - Starting Reading |  |  | AWS meter - Ending Reading